## Specification
Specification: room 19.6 m² — electrical, lighting, ventilation, automation (10.2026)
How to use: change the quantity (B) and price (D) — totals recalculate. Price basis “estimate” — not verified; empty price — TBC. Prices in US dollars, converted from roubles at the Bank of Russia rate of 83.5588 RUB/USD on 1 October 2026; sums rounded to whole dollars.
Item | Qty | Unit | Price, $ | Sum, $ | Price basis
DB board
MCB 6 A 1P, C (QF6, QF7, QF11) | 3 | pcs | 4.19 |  | estimate
MCB 10 A 1P, C (QF9, QF10, QF15) | 3 | pcs | 4.19 |  | estimate
RCBO 16 A 30 mA type A, 1 module (QFD1, QFD3–QFD6) | 5 | pcs | 35.9 |  | estimate
RCBO 10 A 30 mA type A, 1 module (QFD2, bathroom) | 1 | pcs | 35.9 |  | estimate
Impulse relay 16 A, 230 V, with status contact (KL1–KL3) | 3 | pcs | 29.92 |  | estimate
Interface relay, DIN, 24 V coil (KV1–KV3) | 3 | pcs | 8.38 |  | estimate
Comb busbars/jumpers, terminals, blanks (N/PE busbars come with board) | 1 | set | 29.92 |  | estimate
Section subtotal
Sockets and switches (black)
Socket outlet, 4-gang (S1–S5) | 5 | pcs | 17.95 |  | estimate
Single socket: AC, kettle, fridge, boiler (IP44) | 4 | pcs | 4.79 |  | estimate
Double socket IP44 in bathroom | 1 | pcs | 14.36 |  | estimate
Double socket under DB | 1 | pcs | 9.57 |  | estimate
Two-key switch SW1 (bathroom) | 1 | pcs | 7.18 |  | estimate
Push-button switch, 3 buttons, momentary, SW2 | 1 | pcs | 17.95 |  | estimate
Section subtotal
Lighting
Surface-mounted single-phase track 2 m, black | 8 | pcs | 16.54 |  | estimate
Ritter Artline linear 35 W 4000 K, 607 mm, black | 8 | pcs | 33.96 |  | estimate
Volpe ULB-Q276 25 W 3000 K, track spot | 8 | pcs | 9.93 |  | estimate
Smartbuy 20 W IP65, black square (entry) | 1 | pcs | 16.97 |  | estimate
Feron 51920 24 W IP44, black square (bathroom) | 1 | pcs | 42.09 |  | estimate
Above-mirror light IP44 — to be chosen | 1 | pcs |  |  | TBC
Power feeds, end caps, track connectors | 4 | set | 4.79 |  | estimate
Boxes JB1, JB2, bathroom junction box | 3 | pcs | 3.59 |  | estimate
Section subtotal
Cables and conduit
Cable VVGng(A)-LS 3×2.5 | 95 | m | 1.32 |  | estimate
Cable VVGng(A)-LS 3×1.5 | 35 | m | 0.9 |  | estimate
Cable VVGng(A)-LS 5×1.5 (light: DB → SW2, DB → JB1; heater + thermal cut-out) | 8 | m | 1.44 |  | estimate
Twisted pair FTP cat5e (sensors, control) | 50 | m | 0.48 |  | estimate
Black PVC conduit Ø16 w/ draw wire (Ural-Pak) | 20 | m | 0.22 |  | estimate
Black PVC conduit Ø20 w/ draw wire (Ural-Pak) | 25 | m | 0.26 |  | estimate
Black PVC conduit Ø25 w/ draw wire (Ural-Pak) | 100 | m | 0.34 |  | estimate
Black PVC conduit Ø32 w/ draw wire (Ural-Pak) | 15 | m | 0.48 |  | estimate
Conduit clips Ø16/20/25/32 (35 cm spacing) | 440 | pcs | 0.07 |  | estimate
Sleeves in bathroom wall, non-combustible sealant | 4 | pcs | 1.8 |  | estimate
Section subtotal
Ventilation
Duct fan Vents TT PRO 125 (2 speeds, 240/350 m³/h, 110/150 Pa, 25/30 W) | 3 | pcs | 89.64 |  | estimate
Duct heater DVS EKA 125 1ph 1.5 kW (thermal cut-out +50 °C auto / +100 °C manual) | 1 | pcs | 72.28 |  | estimate
Duct filter Ø125 with G4 cassette + spare cassette | 1 | set | 29.92 |  | estimate
Spring-loaded backdraft damper Ø125 | 3 | pcs | 7.18 |  | estimate
Iris damper Ø125 (airflow adjustment) | 3 | pcs | 15.56 |  | estimate
Flexible connector Vents VVG 125 (vibration isolation, 2 per fan) | 6 | pcs | 7.18 |  | estimate
Outdoor grille ALAV 125 (aluminum, angled louvers, mesh) | 2 | pcs | 4.55 |  | estimate
Splitter plate between grilles: composite panel 3–4 mm 180×320, black | 1 | pcs | 5.98 |  | estimate
Diffuser Rodfer DK-125 ChM (steel, matte black, Ø180, adjustable, magnetic mount) | 5 | pcs | 19.99 |  | estimate
Ducts Ø125, bends, tees, clamps, rubber-lined hangers | 1 | set | 59.84 |  | estimate
Section subtotal
Control cabinet CC
OWEN PR200-24.4.2.0 | 1 | pcs | 208.79 |  | estimate
OWEN PRM-24.1 | 1 | pcs | 90.52 |  | estimate
24 V PSU w/ battery charging (Mean Well DRC-100B, 100 W, or equiv.) + 2 batteries 12 V 7 Ah | 1 | set | 131.64 |  | estimate
Contactor KM1 2P 25 A 230 V, power controller U1 0–10 V on heatsink, relays K1–K4 | 1 | set | 113.69 |  | estimate
MCBs QF-T, QF-V, QF-PC, QF-24; terminals, rails, cable ducts, busbars | 1 | set | 71.81 |  | estimate
CC welded enclosure 1000×1060×300: 1.5 mm sheet on a 30×30 tube frame, continuous welds, roof without openings, posts extended 600 mm down, bottom with grille and filter, 2 fans 24 V, powder coating | 1 | set | 203.45 |  | estimate
IP68 cable glands for Ø16–Ø32 conduit w/ adapters, nuts welded into roof | 8 | pcs | 2.99 |  | estimate
CC door: 2 tempered glass panes 4 mm 1000×540 with ground edges, brush seal, double-groove guides, roller, wire rope, bracket with quick-release pin | 1 | set | 59.84 |  | estimate
Linear actuator 24 V, 550 mm stroke, up to 300 N, built-in limit switches + 70×70 cover | 1 | set | 59.84 |  | estimate
Actuator reversing relays (2 pcs), door button on side | 1 | set | 17.95 |  | estimate
Section subtotal
Sensors
iArduino CO₂ RS-485 (NDIR + t + humidity) — room, sensor 2 | 1 | pcs | 57.44 |  | estimate
iArduino climate unit RS-485 (t, humidity, light) — bathroom and cabinet | 2 | pcs | 10.29 |  | estimate
iArduino eCO₂/TVOC RS-485 (SGP30) — odor/smoke in supply, sensor 9 | 1 | pcs | 29.8 |  | estimate
R4DCB08 module: 8 channels DS18B20 → RS-485 Modbus | 1 | pcs | 13.16 |  | estimate
Sealed DS18B20 probe, 2–3 m cable: outdoor and after heater | 2 | pcs | 2.39 |  | estimate
Smoke detector IP 212-39/1 “Agat”, 4-wire, 7–30 V, relay, no sounder (BD1) | 1 | pcs | 10.77 |  | estimate
Differential pressure switch EKF RVG-10-500 (with tubes and fittings): flow SP1, filter SP2 | 2 | pcs | 15.56 |  | estimate
Cabinet door reed switch SQ1 (IO 102-2 or equiv.) | 1 | pcs | 2.39 |  | estimate
USB–RS-485 adapter for setting sensor addresses (one-off) | 1 | pcs | 4.79 |  | estimate
Section subtotal
Computer — for the future, not included in total
Graphics card GeForce RTX 3060 12 GB (new) | 1 | pcs | 0 |  | later
Mini-ITX board with Wi-Fi + CPU + 32 GB + NVMe 1 TB + PSU SFX 550 W + PCIe riser + USB–RS-485 | 1 | set | 0 |  | later
UPS 650–850 VA (new) | 1 | pcs | 0 |  | later
Monitor 15.6″ + VESA mount | 1 | pcs | 0 |  | later
Section subtotal
Climate and video
Air conditioner Midea Persona MSAG4-09HRN8-I, black, 2.6 kW | 1 | pcs | 451.06 |  | estimate
Midea Wi-Fi module for the AC (local control) | 1 | pcs | 29.92 |  | estimate
AC installation: unit on 2 spacers 40×20, 5 cm off the wall (conduits to the cabinet behind it), route ≈4.5 m: copper + cable + drain in one 60×40 trunking for 2.0 m, one sleeve at the bottom of the infill panel, copper above the window, drain drips by the window; bracket: unit behind the glazed sash, bottom ≈30 cm above ground | 1 | set |  |  | TBC
IP camera 4 MP, 2.8 mm, IR, PoE (CAM1 — bullet, CAM2 — dome) | 2 | pcs | 0 |  | later
PoE switch 4+1, DIN rail | 1 | pcs | 0 |  | later
LED strip 24 V blue + profile (cabinet backlight) | 1 | set | 14.36 |  | estimate
Section subtotal
Finishing
Decorative ladder above the radiator: 2 posts 40×40 with base plates to the floor (5 cm from each window edge), 4 bent strips 40×20 with a sharp kink (top one — handrail at 1.70 m), 4 steps 410×160 of bent checker plate 3 mm, post tops at 1.76 m turned into the wall with base plates on anchors, powder coating | 1 | set | 101.72 |  | estimate
Section subtotal
TOTAL for all sections (excl. items without price)

## Cable schedule
№ | Line | From | To | Cable | Conduit | Route, m | Cable incl. allowance, m | Section
1 | Cct 6 — boiler | DB | boiler socket | VVGng(A)-LS 3×2.5 | Ø25 | 3.32 | 4.02 | Bathroom
2 | Cct 3 — bathroom socket | DB | double socket | VVGng(A)-LS 3×2.5 | Ø25 | 4.1 | 4.8 | Bathroom
3 | Cct 3 — loop to LPU | double socket | LPU | VVGng(A)-LS 3×2.5 | Ø25 | 1.05 | 1.45 | Bathroom
4 | Cct 1 — SW1 supply | DB | SW1 | VVGng(A)-LS 3×1.5 | Ø20 | 5.34 | 6.04 | Bathroom
5 | SW1 → light and backlight (one conduit) | SW1 | junction box | 2×(3×1.5) | Ø25 | 3.35 | 7.69 | Bathroom
6 | Box → luminaire | box | luminaire | VVGng(A)-LS 3×1.5 | Ø20 | 0.68 |  | Bathroom
7 | Box → backlight | box | backlight | VVGng(A)-LS 3×1.5 | Ø20 | 1.21 |  | Bathroom
8 | Cct 7 — fridge | DB | fridge socket | VVGng(A)-LS 3×2.5 | Ø25 | 6.28 | 6.98 | Room
9 | Cct 8 — kettle | DB | kettle socket | VVGng(A)-LS 3×2.5 | Ø25 | 6.59 | 7.29 | Room
10 | Cct 9 — DB → S5 | DB | S5 | VVGng(A)-LS 3×2.5 | Ø25 | 6.24 | 6.94 | Room
11 | Cct 9 — S5 → S4 | S5 | S4 | VVGng(A)-LS 3×2.5 | Ø25 | 6.55 | 6.95 | Room
12 | Cct 11 — air conditioner | DB | AC socket | VVGng(A)-LS 3×2.5 | Ø25 | 8.13 | 8.83 | Room
13 | Cct 10 — DB → S1 | DB | S1 | VVGng(A)-LS 3×2.5 | Ø25 | 9.11 | 9.81 | Room
14 | Cct 10 — S1 → S2 | S1 | S2 | VVGng(A)-LS 3×2.5 | Ø25 | 6.49 | 6.89 | Room
15 | Cct 10 — S2 → S3 | S2 | S3 | VVGng(A)-LS 3×2.5 | Ø25 | 8.12 | 8.52 | Room
16 | Spare — socket under DB | DB | socket under DB | VVGng(A)-LS 3×2.5 | Ø25 | 0.36 | 1.06 | Room
17 | Cct 4 + cct 5 → CC | DB | CC | 2×(3×2.5) | Ø32 | 8.66 | 19.32 | Ventilation
18 | CC → bathroom exhaust fan | CC | fan | VVGng(A)-LS 3×1.5 | Ø25 | 3.67 | 3.97 | Ventilation
19 | CC → room exhaust fan | CC | fan | VVGng(A)-LS 3×1.5 | Ø25 | 3.65 | 3.95 | Ventilation
20 | CC → supply fan | CC | fan | VVGng(A)-LS 3×1.5 | Ø25 | 1.72 | 2.02 | Ventilation
21 | CC → heater 1.5 kW | CC | heater (2 cores — thermal cut-out) | VVGng(A)-LS 5×1.5 | Ø25 | 1.61 | 1.91 | Ventilation
22 | Cct 2 — DB → SW2 | DB | SW2 | VVGng(A)-LS 5×1.5 | Ø20 | 0.36 | 1.06 | Lighting
23 | Cct 2 — DB → box JB1 (3 keys) | DB | JB1 | VVGng(A)-LS 5×1.5 | Ø20 | 3.41 | 4.06 | Lighting
24 | JB1 → track T0 (loft) | JB1 | T0 | VVGng(A)-LS 3×1.5 | Ø20 | 1.45 | 1.8 | Lighting
25 | JB1 → track T1 (work) | JB1 | T1 | VVGng(A)-LS 3×1.5 | Ø20 | 0.63 | 0.98 | Lighting
26 | JB1 → track T2 (work) | JB1 | T2 | VVGng(A)-LS 3×1.5 | Ø20 | 0.23 | 0.58 | Lighting
27 | JB1 → track T3 (loft) | JB1 | T3 | VVGng(A)-LS 3×1.5 | Ø20 | 0.8 | 1.15 | Lighting
28 | JB1 → entry luminaire | JB1 | entry luminaire | VVGng(A)-LS 3×1.5 | Ø20 | 1.01 | 1.36 | Lighting
29 | Bus: bathroom humidity sensor → sensor 2 | sensor 1 | sensor 2 | twisted pair FTP cat5e | Ø16 | 3.18 | 3.78 | Sensors
30 | Bus: sensor 2 → CC | sensor 2 | CC | twisted pair FTP cat5e | Ø16 | 7.76 | 8.06 | Sensors
31 | Smoke detector → CC | smoke det. | CC | twisted pair FTP cat5e | Ø16 | 0.28 | 0.68 | Sensors
32 | Light control: DB → box at entrance | DB | box JB2 | FTP cat5e (control) | Ø16 | 2.01 | 2.61 | Sensors
33 | Smoke det. + light control + camera 2 → cabinet (one conduit) | box JB2 | cabinet | 3×FTP | Ø20 | 6.71 | 22.22 | Sensors
34 | Outdoor temperature → cabinet | outdoor probe | cabinet (R4DCB08) | twisted pair FTP cat5e | Ø16 | 2.32 | 2.62 | Sensors
35 | t after heater and odor sensor → drop | supply probe | CC | 2×FTP | Ø16 | 0.08 | 0.96 | Sensors
36 | Supply sensors (t after heater, odor) → cabinet | supply duct | CC | 2×FTP | Ø20 | 0.77 | 2.53 | Sensors
37 | Diff. pressure switch tubes (4 pcs) → cabinet | supply | SP1, SP2 in cabinet | PVC pneumatic tube Ø6 | Ø16 | 1.67 |  | Sensors
38 | Camera 1 → cabinet (side) | camera 1 | cabinet, side wall | twisted pair FTP cat5e | Ø16 | 1.12 | 1.92 | Sensors
39 | Camera 2 → box JB2 | camera 2 | box JB2 | twisted pair FTP cat5e | Ø16 | 0.57 | 0.97 | Sensors
Total by cable type (incl. allowance)
2×(3×1.5)
2×(3×2.5)
2×FTP
3×FTP
FTP cat5e (control)
VVGng(A)-LS 3×1.5
VVGng(A)-LS 3×2.5
VVGng(A)-LS 5×1.5
twisted pair FTP cat5e
PVC pneumatic tube Ø6
Total conduit (route length)
Conduit Ø16
Conduit Ø20
Conduit Ø25
Conduit Ø32
+ incoming cable VVGng 5×6 in Ø32 within the room — 3.6 m

## DB circuits
Circuit | Phase | Device | Cable VVGng(A)-LS | Length incl. allowance, m | Pinst, kW | Load
1 | L1 | QF6 6 A, C | 3×1.5 | 16 | 0.05 | Bathroom light, backlight (SW1)
2 | L1 | QF7 6 A, C | 5×1.5 / 3×1.5 | 11 | 0.5 | Room light: entry, loft, work (SW2)
3 | L1 | QFD2 RCBO 10 A, 30 mA | 3×2.5 | 6.3 | 2 | Bathroom socket, LPU
4 | L1 | QF9 10 A, C | 3×2.5 | 9.7 | 1.5 | CC: supply heater
5 | L1 | QF10 10 A, C | 3×2.5 | 9.7 | 0.6 | CC: fans, PC, UPS, 24 V
6 | L2 | QFD1 RCBO 16 A, 30 mA | 3×2.5 | 4 | 2 | Water heater 2 kW
7 | L2 | QF11 6 A, C | 3×2.5 | 7 | 0.3 | Fridge
8 | L2 | QFD3 RCBO 16 A, 30 mA | 3×2.5 | 7.3 | 2.2 | Kettle
9 | L3 | QFD4 RCBO 16 A, 30 mA | 3×2.5 | 13.9 | 2 | Sockets S4, S5
10 | L3 | QFD5 RCBO 16 A, 30 mA | 3×2.5 | 25.2 | 2.5 | Sockets S1, S2, S3
11 | L3 | QF15 10 A, C | 3×2.5 | 8.8 | 1 | A/C
12 | L3 | QFD6 RCBO 16 A, 30 mA | 3×2.5 | 1.1 | 1 | Socket under DB (spare)
| L1 | Pinst per phase, kW
| L2 | Pinst per phase, kW
| L3 | Pinst per phase, kW

## Inputs-outputs
Channel | Signal | From / to
DI1 | “Entry” light on | KL1 aux. contact (DB)
DI2 | “Loft” light on | KL2 aux. contact
DI3 | “Work” light on | KL3 aux. contact
DI4 | Air flow present | K1
DI5 | Heater thermal prot. OK | K2
DI6 | Fire | BD1 / K3
DI7 | Heater contactor on | KM1 aux. contact
DI8 | Filter clogged | SP2 diff. press.
DI9 | Mains 230 V OK | K4
DI10 | CC door button | button on side panel
DI11 | CC door closed | reed sw. SQ1
DI12–16 | Spare | —
AI1–AI4 | Spare (temperatures now via RS-485) | —
AO1 | Heater power 0–10 V | U1 controller
AO2 | Spare | —
DO1–DO3 | “Press” light: entry / loft / work | KV1–KV3 (DB)
DO4 | Heater enable | KM1 circuit
DO5 | Supply fan | M3
DO6 | Bathroom exhaust | M1
DO7 | Room exhaust | M2
DO8 | Cabinet fans 24 V | M4, M5
DO9 | Smoke detector reset | BD1 power
DO10–DO11 | Computer Power / Reset buttons | PC mobo
DO12 | Cabinet blue backlight | 24 V strip
DO13 | CC door: open | reverse relay → drive
DO14 | CC door: close | reverse relay → drive
DO15–16 | Spare | —
RS-485 №1 | Sensor bus, PR200 is master | 4 iArduino sensors + R4DCB08
RS-485 №2 | Link to computer, PR200 is slave | USB–RS-485 in PC
PC (not PR200) | A/C, cameras CAM1–CAM2 | Midea Wi-Fi (local), PoE switch